## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Suprintending Engineer, EWSS,BHU
Name of Work: Construction of new 14”x8” tubewell , pipeline connectivity along with associated submersible pumps, electrics etc. at Hanuman mandir, SSH, BHU.
Contract No: EWSS/2021-22/WS/ Tubewell Construction/SSH/BHU/ 01
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Total Estimated Cost (in Rs.) |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Price inclucive of GST (in Rs) | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With GST (in Rs) | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Construction of new 14”x8” tubewell , pipeline connectivity along with associated submersible pumps, electrics etc. at Hanuman mandir, SSH, BHU. | BI01010001010000000000000515BI0100001112 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | Drilling of pilot bore 8.5” to 14”with rig machine from ground level (G.L.) to 160 Mtrs. below ground level (B.G.L.) or more. | BI01010001010000000000000515BI0100001113 | 160 | Mtrs. | 2475000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Reaming of pilot bore from G.L. to 50Mtrs. B.G.L. 675 mm dia . | BI01010001010000000000000515BI0100001114 | 55 | Mtrs. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.03 | Reaming of pilot bore from 55 mtrs. B.G.L. to 155Mtrs. B.G.L. or more 450 mm dia . | BI01010001010000000000000515BI0100001115 | 100 | Mtrs. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
2 | Supply & lowering/fixing of the following materials including transportation loading/unloading, welding, jointing, painting etc. of the pipe with two coats of black japan paint at site. | BI01010001010000000000000515BI0100001116 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2.01 | 14” ERW M.S. 6mm thick blind pipe plain ended Tata/jindal/QST make | BI01010001010000000000000515BI0100001117 | 50 | Mtrs. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2.02 | 8” ERW M.S. 6mm thick blind pipe plain ended Tata/jindal/QST make | BI01010001010000000000000515BI0100001118 | 50 | Mtrs. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.03 | 8” ERW M.S. 6mm thick slotted pipe plain ended with slot size 3”x 1/16” / 3”x3/64” Tata/jindal/QST make as per site requirement. | BI01010001010000000000000515BI0100001119 | 50 | Mtrs. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.04 | Tubewell accessories such as well cap , well clamp, well plug, M.S.ring , centre guide, reducer etc as per specification given below. | BI01010001010000000000000515BI0100001120 | 1 | Set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
2.05 | Supply & Shrouding of Lal Kuan pea gravel duly screened & washed-Size 1/16” to 3/16” | BI01010001010000000000000515BI0100001121 | 45 | Cu Mtrs. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
3 | Development of tubewell air compressor 250/350 PSI capacity as per site requirement. | BI01010001010000000000000515BI0100001122 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
3.01 | For a period upto 50 HRS.. | BI01010001010000000000000515BI0100001123 | 50 | Hrs |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3.02 | Additional period beyond 50 HRS. But up to 75 HRS. | BI01010001010000000000000515BI0100001124 | 25 | Hrs |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
4 | Development of tube well by O.P. unit of 4 cusec capacity. | BI01010001010000000000000515BI0100001125 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
4.01 | For a period upto 50 HRS. | BI01010001010000000000000515BI0100001126 | 50 | Hrs |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
4.02 | Additional period beyond 50 HRS. But up to 75 HRS. | BI01010001010000000000000515BI0100001127 | 25 | Hrs |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6 | Transportation charges of machine, compressor, O.P. unit etc. To site and back including site ,approach way preparation, Trimming of trees at site , manual digging (JCB strictly prohibited)of pit for drilling water etc. | BI01010001010000000000000515BI0100001128 | 1 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
7 | Conducting geophysical well logging of borehole drilled including submitting the report complete as per direction of engineer incharge. | BI01010001010000000000000515BI0100001129 | 1 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
8 | Construction of10Ft x10 Ft x4Ft brick masonry platform including plaster work for safety of tube well and make good other dismantled items during site, approach way preparation and tubewell construction etc. after completion of work as per instruction of engineer incharge. | BI01010001010000000000000515BI0100001130 | 1 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9 | Supply and filling of chopan/ganga sand in existing defunct tube well. | BI01010001010000000000000515BI0100001131 | 1 | Job |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
10 | Supply and installation of 6” M.S. column pipe with welded flange C -(Heavy) class pipe of 150mm nNB Tata/QST/Jindal make for submersible pump . Wall thickness of pipe -5.4mm, Length-3.0 Mtrs. Flange O.D,P.C.D.,Hole dia as per I.S.Standard Flange Thickness-16 mm Note-1-There will be grooving in each flange for submersible cable. 2-4 Nos. M.S. triangular clit should be welded in each flange. 3- Flange should be welded in right angle 4-Each column pipe should be painted by anticorrosive black paint after fabrication & inspection by engineer incharge. | BI01010001010000000000000515BI0100001132 | 12 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
11 | Supply & installation of KSB pumpset 41H.P. model BPHA384+HBC pump type BPHA4 motor type HBC413 suitable for star –delta operation. | BI01010001010000000000000515BI0100001133 | 1 | Set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
12 | Supply and installation of 40HP/50HP star delta starter panel as per technical specification as detailed in enclosed Annexure-1 | BI01010001010000000000000515BI0100001134 | 1 | No. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
13 | Supply and installation 16.00Sqmm product code: 19803091 finolex three core flat cables with bare bunched copper conductor insulated with PVC for submersible pump motor with voltage grade up to 1100 Volt generally confirm to IS694:1990. | BI01010001010000000000000515BI0100001135 | 250 | Mtrs. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
14 | Supply and laying of150 mm dia centrifugally cast(spun) ductile iron pipe class K-7 inside cement mortar lining and outside zinc coating with finishing layer of bitumen paint confirming to Is:8329:2000 ,Make- Electrosteel / jaibalajee with necessary fitting confirming to IS;9523:2000for push on jointing, Make –KESIN/Keseriwal including earth work in manual excavation(excavation by JCB strictly prohibited) of trenches in brick edge/ bitumen road etc. and fitting , fixing, jointing valves, specials , cc thrust block, making branch connection with existing running water main etc without interruption of water supply in premises, filling of trenches with excavated materials in layer after successfully testing of pipeline etc with make good of surface by brick layer/ cc flooring etc complete in all respect as per instruction of engineer in charge. The sluice valve, N/R Valve and Tee etc required for branch connection will be provided by the purchaser free of cost. | BI01010001010000000000000515BI0100001136 | 50 | Mtrs. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
15 | Construction / revamping of masonry chamber 120x120x100 cm inside, in class designation 75 brick work in cement mortar 1:4 with 100mm thick RCC split top cover finished with a floating coat of neat cement complete as per instruction of engineer in charge for 150/200 mm sluice valve. | BI01010001010000000000000515BI0100001137 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information